Optimal Sizing of a Solar Water Pumping System for Koyli Alpha Village, Senegal

Badara MBOW*, Amy SADIO, Bertrand TCHANCHE FANKAM, Senghane MBODJI*

Research Team in Renewable Energies, Materials and Laser of the department of Physics, Alioune DIOP University of Bambey, Bambey, Senegal.

| Article Info |  | ABSTRACT |
| --- | --- | --- |
| Article history: Received Revised Accepted |  | In this paper, two sizing methods applied to the solar water pumping system designed for the Koyli Alpha village located in the Ferlo zone in the north of Senegal were developed and confronted. The intuitive sizing method allows to determine the size of different components. The numerical sizing method was developed for optimal operation. Two models of the solar cell temperature were used. The first one depends only on the ambient temperature and the second one combines wind speed and ambient temperature. Simulations’ results show that the numerical sizing method, which uses the second cell temperature model gives the best performance. It yields a reduction of the batteries size and a total life cycle cost found of 54% and 32%, respectively in comparison with the intuitive sizing method. |
| Keywords: Water pumping Cell temperature Isoreliability curves Loss of power supply probability |  |  |
|  |  | This is an open access article under the CC BY-SA license. |
| Corresponding Authors: Badara MBOW and Senghane MBODJI, Research team in renewable energies, materials and laser of Department of Physics, Alioune DIOP University of Bambey; Bambey, Senegal, Email: badara.mbow@uadb.edu.sn, senghane.mbodji@uadb.edu.sn |  |  |

- INTRODUCTION

The growing world population is leading to a high energy demand. The gloal energy supply is largely covered by fossil fuels. Nevertheless, fossil fuels has a nunber of drawbacks. Fossil fuels reserves are depleting and their use has negative impacts on the environment and on health as well [1]. They are responsible of the global warming and climate change and poor air quality. Developing African nations as the rest of the world rely heavily on fossil fuel to cover their energy demand [2]. They have high solar irradiation, and are progressively adopting renewable energy technologies, which have lower environmental impacts[3]. For example, Algeria has more than 3000 hours of sunshine per year and the yearly average of daily solar irradiation in Adrar, ranges from 5 up to 7 kWh/m²/day [4]. In Senegal, an average 5.8 kWh/m² per day was recorded. This solar energy potential encouraged the government to invest in large scale solar power plants (Bokhol, Malicounda, Mekhe, and Merina) [5], and promote the use of solar energy technologies in remote areas. In literature, many authors considered monthly or annual average values of meteorological data in their sizing methods.  Some authors had done theirs sizing by intuitive methods. They mentioned several challenges among which the lack of meteorological data and the oversizing of PV systems which increases the investment cost. In order to optimize solar PV systems, numerical sizing methods are often used. Bouzidi et al. [6], used his method and reduced the cost of a PV system which presented a good reliability. In their work, they used hourly irradiation of Adrar, in Algeria and the results showed a very low LPSP means less energy loss. Despite the  advances noted in photovoltaic technologies, it is important to optimize solar module production by acting on the temperature of the solar cell. Some authors have invetigated parameters which increase the energy generation by reduing cell temperature. It is the case in ref.[7], where authors used the mean wind speed, for two seasons: the dry season (November-May) and the rainy season (June-October) to evaluate the mean wind speed. The regimes in the sites of Kayar, Potou, Gandon and Sakhor were determined by using the data collected at two heights for each site. The monthly average wind speed obtained in the Potou site were 5.65 m/s and 4.74 m/s for dry and rainy seasons, respectively. Results showed that dry season is characterized by strong wind regimes, while, the rainy one is characterized by lower mean wind speeds. Ouammi et al. [8] evaluated also the wind energy potential using the wind speed data recorded during 7 years (2002 to 2008) from four meteorological stations in Liguria region, in Northwest of Italy. They showed that the wind speed regimes is a fundamental factor to evaluate the wind potential in these four localities. The generated power depends on the wind speed. These data allowed to evaluate monthly and seasonal variations of wind speed, as well as the height of wind speed and the wind potential. The probability distribution function of wind speed is fundamental to assess the wind potential in order to find the performance of a wind system for a given site. Authors noted the impact of wind speed in these expression’s model of cell solar temperature during different seasons and localities, they concluded that the wind speed decreases the production and reduces the cell solar temperature. Faye et al. [9] described in their studies the importance of the second expression’s model of solar cell temperature using the wind speed and the ambient temperature compared to the first expression’s model of solar cell temperature, which depends only on the ambient temperature and the solar radiation. Their study revealed that the wind speed is an important factor, which decreases the solar cell temperature. Their results had been confirmed by F. A. Kamgba et al. [10] who showed that, the power increases with the wind speed. This paper focuses on the comparison of two sizing methods applied to a PV pumping system based in Kyoli Alpha a small village located in the norh of Sengal. The methods will be presented in the next section and the results of the simulation discussed.

- MATERIALS AND METHODS

In order to size, the solar photovoltaic systems, there are intuitive, numerical, analytical and artificial intelligence sizing methods [11] [12]. Here, we present two models of cell temperature using the hourly data of the village of Koyli Alpha. These data are exploited in the numerical sizing method. Two models of cell temperature are used and compared for the years 2016 and 2017. The second part is about of the intuitive method for delimiting workspace i.e the size of the components. For the optimization of the system, numerical sizing method was applied using instantaneous meteorological data.

2.1.   Solar cell temperature modelling

Two models are used to calculate the cell temperature for the years 2016 and 2017. The first model of the cell temperature is given by equation (1) [13-14]:

(1)

): instantaneous cell temperature of the first model;

is the time expressed in hours;

: nominal operating cell temperature;

: instantaneous ambient temperature;

: reference irradiance.

The second model of the cell temperature is expressed in equation (2) [15, 9]:

(2)

: instantaneous cell temperature of the second model;

, and: empirical coefficients of the second model of cell temperature;

is the instantaneous wind speed.

After using the regression model, we found empirical coefficients. Hence ,and. This leads to a new expression of solar cell’s temperature located in the ferlo zone. This expression is described by the first expression’s model of the solar cell temperature, which becomes:

(3)

2.2.   Solar cell’s temperature evolution

The first model of solar cell temperature depends only on the ambient temperature while the second model of solar cell temperature takes into account both the ambient temperature and the wind speed. We present in figures 1 and 2 the monthly average variation of the solar cell temperatures obtained from these two models in 2016 and 2017, respectively.

Figure 1: Annual mean monthly cell temperature from the two models in the year of 2016

Figure 2: Annual mean monthly of solar cell temperature from the two models in the year of 2017

The variation of the solar cell temperature in these two models is taken over a range of 24 months between 2016 and 2017. In the literature, some authors utilized the model n°1 based on the ambient temperature and the solar radiation to estimate the values of the solar cell temperature [13, 14]. Our study showed that the model n°1 of solar cell temperature almost reaches its maximum value, 67.2°C, in April and decreases randomly until reaching the minimum value 31.6°C, in August for the year 2016. While, the model n°2 gives a maximum value, 62.5°C, in October and a minimum value 37.5°C, in August. The temperature Tc1 (t) is smaller than Tc2 (t) in all months of the year 2016 except in August, where we recorded a higher ambient temperature, equal to 31.7°C. This result can be justified by a heavy rainfall. For the year 2017, Tc1 (t) has a maximum value, equal to 65.5°C in April and a minimum value estimated to 46.7°C in November.  Tc2 (t)  recorded a maximum value, equal to 62.6°C in May and a minimum value equal to 46°C in December. The analysis of these two models revealed that the model using the wind speed is more interesting because it provides the lowest values ​​of solar cell temperatures during all months of the year 2017.

- SIZING METHODS FOR PV SYSTEMS

3.1.   Intuitive methods

Intuitive sizing methods give the size of solar photovoltaic system components. The use of the intuitive sizing method allows to find the total power capacity of PV field required to satisfy the demand of Koyli Alpha site and the requisite battery capacity for two days without sunshine and during night. There are two different approaches of sizing on the intuitive methods. The first approach is the worst month approach, which consists of using the month having the lowest irradiations in the year. Leye et al. considered December as the worst month in their study done in Ndem, Senegal [16]. Sadio and al. opted for the second approach, ie, the use of mean values such as the annual average monthly data in the sizing process, to ultimately find out an optimal photovoltaic solar systems [5]. According to the monthly mean data taken between August 2015 and August 2018, the month of December 2017 recorded the lowest value of solar radiation, therefore we adopt the approach of worst month. The intuitive methods use inherent formulas for each component. The sizes of photovoltaic field and batteries storage are given by equation (4) and (5) respectively [17]:

(4)

is the daily energy, estimated to 133640 Wh; is the peak power and is equal to 530044 WP; is the reference irradiance that is evaluated to 1000W/m²; is the monthly average of daily solar irradiation estimated to 3.877 kWh/m²/day, recorded in December 2017 from the meteorological station of Widou, is the loss factor = 0.65. It takes into account all the losses of system, namely the different efficiencies of components, resistive and PV cell temperature losses.

(5)

N  is the number of the autonomous days, V b  corresponds to the voltage of the system and is equal to 48V, DOD(Deep of Discharge) is estimated at 0.80 for acid batteries, ηb is the efficiency of the storage battery, evaluated to 80%. It is important to estimate total life cycle cost (TLCC) of the system. It appears to be the best indicator to evaluate the total cost of the solar PV system rather than using the investment cost. In the TLCC five components are used: the PV panels, the pump, the motor AC, the storage battery, and the inverter. Moreover, the total lifecycle cost (TLCC) integrates the investment cost, the replacement cost and the maintenance cost .see  equation (6) [18]:

(6)

The initial total cost is the sum of all components of our PV system and the price of the installation, and the civil works. The initial total cost is given by the following equation (7) [18]:

(7)

C PV  and C Unit, PV are the total capacity and the unit cost of the PV array, respectively;

C Unit, b is the unit cost of the battery;

C inv   and C Unit, inv are total capacity and unit cost of the inverter, respectively;

C pump   and C Unit, pump are total capacity and unit cost of the pump, respectively;

C mot and C Unit, mot   are total capacity and unit cost of the motor, respectively;

C0 represents the total constant cost which includes both the civil work and the installation cost. All these components required replacement during the system lifetime taking into account the storage battery, the pump, the motor AC and inverter. Thus, the replacement cost CR is given by equation (8) [18]:

(8)

The values of the inflation rate () and interest rate () of the components of the system were considered in this work.  represents the unit component cost of the storage battery, the pump, the motor AC, and the inverter;means the nominal capacity of the replacement system components; and refers to the number of replacement of each component over the system life period ().

The operation and maintenance cost are defined by equations (9) and (10) [18]:

IR ≠ FR                                                           (9)

for IR = FR                                                                                                         (10)

is the operation and maintenance cost in the first year.

3.2.   Numerical sizing method using instantaneous meteorological data

Before elaborating the sizing algorithm to find the best combination of components, we deal with the parameters. The model adopted to describe the PV generation gives the instantaneous photovoltaic energy after taking into account the solar cell temperature expressed here in two different models as presented above. Hourly data of the ambient temperature are used, the solar radiation, and the wind speed were obtained from weather station of Koyli Alpha. Our objective is to determine which of these two models of solar cell temperature is the most appropriate for the numerical sizing method. Hence the instantaneous energy production of the PV array for the two models is given in equation (11) and (12) respectively:

(11)

(12)

E PV, 1 (t): the instantaneous photovoltaic energy field for first model;

E PV, 2 (t): the instantaneous photovoltaic energy field for the second model;

A PV: the area photovoltaic field;

η inv  and η W   are the inverter and wire yields, respectively;

η ref  : reference yield;

β: the temperature coefficient.

Replacing the expressions of (1) and (3), in equations (11) and (12), we end up with the following equations (13) and (14) respectively:

(13)

and

(14)

The instantaneous energy difference between energy produced by the modules and the daily energy load expressed from equations (15) and (16) for the two models respectively allows knowing the batteries behavior. The instantaneous energy difference is calculated using the following equations (15) and (16), respectively [17]:

(15)

and

(16)

and correspond to the instantaneous energies difference given by the expression of the models n°1 and n°2 of the solar cell temperature, respectively, Ed is the daily load energy. If the valuesand   are  less than zero, and the batteries have being discharged, then, the instantaneous energy stored is calculated for first and second models respectively from equations (17) and (18), respectively [15 17]:

(17)

and

(18)

If the values ofand  are greater than zero, respectively, then, the batteries are being charged, and the instantaneous energies stored, in the batteries, are calculated using equations (19) and (20) [17], for model 1 and model 2, respectively:

(19)

and

(20)

In order to protect the batteries against overcharge, discharge, and drastic reduction of its life cycle, instantaneous energy stored in the battery is subject to the given restriction [19]:

(21)

(22)

and  are the maximum and minimum energies of the batteries.

The instantaneous loss of power supply which represents the missing energy quantity to satisfy the load demand during 24 hours is computed for the two models by equations (23) and (24).

(23)

and

(24)

The instantaneous loss of power supply probability represents the percentage of power supply that is not able to satisfy load demand and is obtained by summation of all instantaneous loss power supply at specific time over the load energy, in accordance with equations (25) and (26)  for the two models respectively:

(25)

and

(26)

LPSPindicates the reliability of power supply to load. If  LPSP(t) is equal to 0, it means that the system totally satisfies the load demand while on the other hand, if LPSP is equal to 1, it means that the load demand is not satisfied by the PV system. An LPSP(t), which is between 0 and 1 means that the supplied power cannot fully cover the load demand because there are an insufficient energy production from the PV array and not enough energy stored in the batteries [19]. The objective is to calculate the storage capacity corresponding to each PV capacity value, considering all these operating conditions. The PV capacity varies from a minimal value equal to the unitary PV module capacity, up to a maximal value corresponding to the PV power found by applying the intuitive method. Figure 3 shows the sizing algorithm of numerical method.

Figure 3:  Sizing algorithm of numerical method for the two expression’s models of solar cell temperature

- RESULTS AND DISCUSSIONS

Simulation results gave a total PV array capacity, equal to 53,044 kWp and a storage system capacity, of 6,960 Ah. If we increase this storage capacity about 20% to take into account the depth of allowed discharge, it grows to 8,352 Ah. The Total Life Cycle Cost (TLCC) of the pumping photovoltaic solar system is about € 920,304.8998. In this study the models were implemented in Python software. Results obtained from for the two models are shown in figures 4, 5, 6 and 7. Figure 4 shows the different combinations of PV array capacity and the storage system capacity at different reliability levels, called isoreliability curves, when the first expression’s model of the solar cell temperature is utilized.

Figure 4: Different PV/battery combinations with numerical sizing method using the first expression’s model of solar cell temperature.

The objective of this work is to look for a good combination panel/battery in order to have a good reliability and a reduction cost. In this optimization, we worked with the probabilistic approach using hourly data in the energetic photovoltaic model. We remarked that the batteries capacity increases inversely proportional with photovoltaic capacity. It means that, during the sunnies days, the photovoltaic field ensures the energetic production, therefore, batteries supply load during night and the days without sunrise. This study is done between 10 am and 3 pm, and we observed that the best reliability corresponding to the best production in capacity (photovoltaic/batteries). Among the isoreliability curves, we chose the one which corresponds to the lowest loss of power supply probability to find the best PV/battery combination. It depends on high power produced by panels and batteries in the PV system. The values of LPSP vary between 0.026 and 0.11.                                                                                                                                                                                                                           The best PV/battery combination which satisfies a reliability level of 97.4% is given in figure 5.

Figure 5: Different PV/battery combinations with numerical sizing method using the first expression’s model of the solar cell temperature at LPSP equal to 0.026

From figure 5, it is noted that a value of total PV array capacity of 49,250 Wp necessitates a storage system capacity of 2,700 Ah. If we increase this storage capacity about 20 % to take into account of the depth of allowed discharge, it grows up to 4,680 Ah. The Total Life Cycle Cost (TLCC) of this combination is 143,477.268 EUR. The proposed sizing method enabled to reduce the number of batteries needed by the PV system to 68 % and the TLCC to 40 %, with only 0.026 of LPSP, when compared to intuitive method. Figure 6 presents different combinations of PV/battery at different reliability levels using the second expression’s model of the solar cell temperature.

Figure 6: Different PV/battery combinations with the numerical sizing method using the second expression’s model of the solar cell temperature.

The values of LPSP, from figure 6, vary between 0.62 and 0.0197. When the value of LPSP is 0.62, we record many losses energy, which lead to a poor reliability.  For a constant value of LPSP, the batteries capacity vary conversely proportional, the batteries increase and panels capacity decrease. For example, for a LPSP equal to 0.0197, the best combination is found with the lowest TLCC. The results of our study are compared to a work done in Sohar region, in Oman. In this study, H. A. Kazem et al utilized geographic, climatic and sunshine coordinates as inputs of photovoltaic/battery system [20]. Theirs results  generated a good reliability of 98.7% ,ie a LPSP equal to 0.013 while our study applied in Koyli Alpha site has  given a reliability of 98.03% corresponding to a LPSP equal to 0.0197 when, the second expression’s model of the solar cell temperature is used. The best PV/battery combinations that satisfies a reliability level of 0.0197 are shown in Figure 7.

Figure 7: Different PV/battery combinations with numerical sizing method using the second expression’s model of the solar cell temperature at LPSP equal to 0.0197

From figure 7, the best PV/battery combination corresponds to a value of total PV array capacity of 51,080 WP and at a storage system capacity of 3,847 Ah. If we increase this storage capacity about 20 % to take into account of the depth of allowed discharge, it grows to 4,680 Ah. The TLCC of this combination is 163,917 EUR. The proposed sizing method using the second expression’s model of cell temperature enables to reduce the number of battery needed by the PV system by 54 % and the TLCC by 32 %, at a LPSP equal to 0.019 of LPSP against the intuitive method. Amy Sadio et al., in their researches, compared the intuitive and numerical methods and the results found that the storage capacity decreases until to 25% and permitted to reduce the TLCC to 49% with numerical method [21]. In [22], B. Ould Bilal et al. had adopted a sizing methodology of a hybrid solar / wind / battery systems using a multi-objective genetic algorithm to minimize cost and increase reliability. The authors worked with hourly solar irradiation, temperature and wind speed data from Potou located in the northwest coast of Senegal and are collected for one year. Compared to the case study applied in one region of Malaysia using data of the year 1999, W.X. Shen kept the load demand constant and fixed the LPSP at 1%. Therefore, in [23], W.X. Shen simulated operating a solar photovoltaic system on MATLAB, and the results generated a ratio battery / panel equal to 0.18 Ah /WP while in our study, the first expression’s model generated a ratio battery / panel equal to 0.095 Ah / WP. The results obtained showed that the cost of the optimal configuration decreases by 25% when the probability of loss of power supply (LPSP) goes from 0% to 1%. The reliability of our solar photovoltaic water pumping systems system can be justified by the use of hourly weather data of Koyli Alpha site. To show the importance of taking into account the parameters, which can influence the PV system performance, two expression’s models cell solar temperature are considered. In terms of reliability, the second model of cell solar temperature, which integrates wind speed, is better than the first model of cell solar temperature, which doesn’t consider the wind speed influence. Indeed they provided LPSP values, equal to 0.0197 and 0.026, respectively. The convection of wind speed is a cooling factor of the solar cell, this confirms the effectiveness of numerical method using expression’s second model of solar cell temperature.

- CONCLUSION

The main goal of this study was to find an optimal response for the energy demand of a water pumping system installed in Kyoli Alpha. We used an intuitive sizing method allowing to find the size of the photovoltaic array and the battery capacity. In order to optimize this system, we elaborated a numerical sizing method which used hourly meteorological data and two expression’s models of the solar cell temperature. These models were applied to the energy model in order to reduce the system cost and optimize the technical reliability. The first model of the solar cell temperature is based on the ambient temperature and the second one is expressed as a function of the ambient temperature and the wind speed. The comparative study showed that the numerical sizing method that uses the second expression’s model is more accurate. Its lowest LPSP is of 0.0197 against 0.026 for the numerical sizing method based on the first model of the solar cell’s expression temperature. Finally, the lowest LPSP obtained gives the best reliability. The best combination panels/battery is the one which presented the lowest cost. The numerical sizing method using the second expression’s model of the solar cell temperature in comparison with the intuitive method yield a reduction of 54% for batteries of and 32% on TLCC.

REFERENCES

[1] O. Bilal et al., ’’Methodology to size an optimal standalone hybrid solar-wind-battery system using genetic algorithm,’’ International Journal of the Physical Sciences, vol. 7, issue 18, pp. 2647-2655, 2012.
[2] M. S. K. Mohamadou et al., ‘’Photovoltaic water pumping system in Niger’’, Chapter 7, http://dx.doi.org/10.5772/54790

[3] R. Krishnan et al., ‘’Modelling of stand-alone photovoltaic systems: a review’’, International Journal of Advanced Research, vol. 2, issue 8, pp. 471-476, 2014

[4] Maafi., ‘’A survey on photovoltaic activities in Algeria‘’, Abdus Salam International Centre for Theorical Physics, Miramare-Trieste, vol 20, issue 1, pp. 9-17, May 2000.

[5] A. Sadio et al., ‘’Analysis of meteorological data for applications in Ngoundiane’s site‘’, EAI Endorsed Transactions on Collaborative Computing, vol. 3, issue 12, 06 2017 - 10 2017

[6] B. Bouzidi et al., ‘’Optimisation du dimensionnement des systèmes de pompage‘’, Revue des Energies Renouvelables, vol. 19, issue 4, pp. 681 – 695, 2016

[7] B. O. Bilal et al., « Economic analysis of wind electricity generation in the northern coast of Senegal », International Journal of Metrology and Quality Engineering., vol. 5, 302, 2014

[8] A. O. H. Dagdougui et al., ‘’Monthly and seasonal assessment of wind energy characteristics at four monitored locations in Liguria region (Italy) ‘’, Renewable and Sustainable Energy Reviews, pp. 1959–1968, 2010

[9] M. Faye et al., ‘’Choice of Site for the installation of photovoltaic solar power plants in Senegal: consequences on electricity production‘’, Journal of Power and Energy Engineering, vol. 5, pp. 109-118, 2017.

[10] F. A. Kamgba et al., ‘’Effects of some meteorological parameters on wind energy », AJOPACS, vol. 4, issue 1, pp. 1-7, 2017

[11] M. Sidrach-de-Cardona et al., ‘’A simple model for sizing standalone photovoltaic systems‘’, Solar Energy Materials and Solar Cells, vol. 5, pp. 199-214, 1998

[12] A. Mellit et al., ‘’Artificial intelligence techniques for sizing photovoltaic systems: A review’’, Renewable and Sustainable Energy Reviews, vol. 13, issue 2, p. 406-419, 2009.

[13] H. A. Kazem., ‘’Feasibility of photovoltaic systems in Oman’’, 2015 1st Workshop on Smart Grid and Renewable Energy, SGRE 2015

[14] B. E. B. Bi et al., ‘’Modélisation des composants d’un système hybride panneau photovoltaïque – stockage d’énergie via l’hydrogène batteries’’, European Scientific Journal, Vol.14, issue.3, January 2018,

[15] D. Faiman, ‘’Assessing the outdoor operating temperature of photovoltaic modules», PROGRESS IN PHOTOVOLTAICS: RESEARCH AND APPLICATIONS, vol. 16, pp. 307–315, 2008

[16] S. N. Leye et al., ‘’Optimum sizing and exploitation of Ndem’s solar plant production », Proceedings of 26th European Photovoltaic Solar Energy Conference and Exhibition, Munich, Germany (2016)

[17] A. Sadio et al., ‘’New numerical sizing approach of a standalone photovoltaic power at Ngoundiane, Senegal’’, EAI Endorsed Transactions on Energy Web and Information Technology, vol. 5, issue 16, 12 2017 - 01 2018

[18] H. M Ridha et al., ‘’Optimum Design of a Standalone Solar Photovoltaic System Based on Novel Integration of Iterative- PESA-II and AHP-VIKOR Methods’’, Processes, 8(3), 2020,

[19] T. Khatib et al., ‘’A review on sizing methodologies of photovoltaic array and storage battery in a standalone photovoltaic system », Energy Conversion and Management, vol. 120, pp. 430-448, 2016

[20] H. A. Kazem et al., ‘’Sizing of a standalone photovoltaic / battery system at minimum cost for remote housing electrification in Sohar, Oman’’, Energy and Buildings, vol. 61, pp. 108–115, 2013.

[21] A. Sadio et al., ‘’A comparative study based on the Genetic Algorithm (GA) method for the optimal sizing of the standalone photovoltaic system in the Ngoundiane site », EAI Endorsed Transactions on Energy Web and Information Technologies, vol. 6, issue 21, , 09 2018 - 01 2019

[22] B. O. Bilal et al., ‘’Multi-objective Design of PV-Wind-Batteries Hybrid Systems by Minimizing the Annualized Cost System and the Loss of Power Supply Probability (LPSP)’’, pp. 861-868, », February 2013.

[23] W.X. Shen., ‘’Optimally sizing of solar array and battery in a standalone photovoltaic system in Malaysia’’, Renewable Energy, vol. 34, pp. 348–352, 2009

BIOGRAPHIES OF AUTHORS (10 PT)

|  | Badara MBOW is a PhD student at Alioune Diop university of Bambey, Senegal. At university, he integrated the Interuniversity Master of Renewable Energies. He has been starting to study the different sources of renewable energies and focused a big part of his study in solar energy. For finishing his master, he worked on the following subject: Empowerment in solar energy of village of Baol: NDEM. In this study, he had done the design of an autonomous photovoltaic power station to ensure supply of electricity from the village of NDEM. In 2018, he began his PhD study at Alioune Diop university of Bambey. Objectives of his thesis are : to size a photovoltaic solar water pumping system for empowerment of the drilling in the great green wall, to study two types of water pumping system, namely: autonomous solar systems (with batteries or/and with supercapacitors) and solar systems without storage energy (batteries or/and with supercapacitors). In this thesis, the objective is also to make a comparison of these two systems to see which is the most profitable that is, to have a view on reliability and cost. Finally, his last objective is to compare a solar PV pumping systems to a diesel pumping systems. |
| --- | --- |
|  | Dr Sadio is a Postdoc scholar & teaching assistant in the dept. of Physics, at the Alioune Diop University. She holds a BSc and a MSc in Physical Science from Alioune Diop University, in Senegal. In 2018, she received her PhD in Physics from the Cheick Anta Diop University, Senegal. She is specialized in renewable energies, and solar energy in particular. She worked on the design and simulation of a standalone photovoltaic systems using numerical methods and Genetic Algorithm (GA). She published several papers in indexed jounals. The first paper analyses meteorological data for photovoltaic applications, and in the second one, a new numerical sizing approach of a standalone photovoltaic power is investigated. The third paper regards a comparative study based on Genetic Algorithm for the optimal sizing of standalone photovoltaic systems. The fourth paper is focused on the sizing of a standalone photovoltaic water pumping systems. Her current and future works are centred on the research for a solution to make more reliable and economically viable the renewable energy systems and meet the challenges of climate change by using the Artificial Intelligence Techniques. |
|  | Dr. Bertrand TCHANCHE is holding a position of Assistant Professor in the Dept. of Physics at the Université Alioune Diop de Bambey, Senegal. He held previous positions at Université de Lorraine and ESIEE-Amiens (France). His main research is in the field of Energy and Environmental Engineering. He works on a wide range of topics: organic Rankine cycles for power generation, analysis of energy systems, transportation systems, classical and quantum thermodynamic systems, energy and atmospheric pollution, energy governance and the anthropology of electricity. He has edited three books and published several papers in international journals as well as in many conference proceedings. He took part in several international projects and is member of many organizations. He acts as external expert for many international organizations, is member of the editorial borad and reviewer for several international journals. |
|  | Senghane MBODJI is a Professor at Alioune Diop University, Bambey, Senegal. He is a specialist of Semiconductor Physics applied to Solar Energy. He holds two PhDs. He is an author or co-author of more than sixty publications in his field. To this end, his works are based to the concept of junction recombination velocity which permits me to determine all operating points of the solar cell: from the open circuit operating point to the short-circuit one. He used the steady state operating conditions, the transient state defined on two steady state conditions or the frequency dynamics state in 1D and 3D modeling studies. These studies helped him to calculate, based on the concept of “junction recombination velocity”, the solar cell power, the open circuit photo-voltage, the effective diffusion length of carriers, the intrinsic junction recombination velocity which is related carriers lost to the junction of the solar cell, the back surface recombination velocity of the solar cell, the shunt and series resistance, to make simulations and validate the electric circuit types equivalent to the solar cell. A study on the effect of grain size and grain boundary recombination velocity on Shunt and series resistance has been made via the junction recombination velocity at the junction (Sf). All these techniques have been used published in journals and conferences. And now, until 2013, he is working on the sizing of solar power plant, the others renewable energy sources such as wind and biomass, the Internet of Things (IoT) applied to energy, the waste management and sanitation. |